| West 6120 1/16 DIN Easy Use Controller |  |
| --- | --- |

|  | The West 6120 is a full featured 1/16 DIN controller. Designed for applications requiring protection from operator errors, setpoint adjustment can be locked or limited to a narrow band. |  |
| --- | --- | --- |
|  | - Tamper proof | - Heat/Cool operation |
|  | - Two process alarms | - Ramping setpoint |
|  | - Loop alarm | - Dual setpoint selection |
|  | - RS485 comms | - Configuration via PC |

## Technical Data

| Features |  |
| --- | --- |
| Control Types | Full PID with Auto Pre-tune, Self-tune, Manual Tuning, or On-Off control. Heat only or heat/cool mode |
| Output Configuration | Up to 3 Total. Max 2 for control (Heat/Heat & Cool), max 2 for Alarms, max 1 for retransmit Process Value or Setpoint |
| Alarm 1 & 2 Types | Process high, process low, SP deviation, band, logical OR and hysteresis. Also 1 loop alarm |
| Human Interface | 2 button operation, dual 4 digit 10mm & 8mm high LED displays, plus alarm indicator |
| Setpoint Locking | Front panel setpoint adjustment – Full, limited or none (selectable) |
| PC Configuration | Configuration via PC only. Dedicated config socket (controller comms option not required) |
| # Input |  |
| Thermocouple | J, K, R, S, T, B, L, & N. |
| RTD | 3 Wire PT100, 50 per lead maximum (balanced) |
| DC Linear | 0-20/4-20mA, 0-50/10-50mV, 0-5/1-5/0-10/2-10V. Scaleable -1999 to 9999, dec point available |
| Impedance | >100M for Thermocouple and mV ranges, 47K for V ranges and 4.7 for mA ranges |
| Accuracy | +/- 0.25% of input span +/- 1 LSD (T/C CJC better than 0.7°C) |
| Sampling | 4 per second, 14 bit resolution approximately |
| Sensor Break Detection | <2 secs (except zero based DC ranges), control O/P’s turn off, high alarms activate for T/C and mV ranges, low alarms activate for RTD, mA or V ranges. |
| # Outputs & Options |  |
| Control & Alarm Relays | Contacts SPDT 2Amp resistive at 240V AC, >500,000 operations |
| Control SSR Outputs | Drive capability >4.2V DC in 1K (10V 500 version available) |
| Solid State (Triac) Outputs | 0.01 to 1 Amp AC 20 to 280V, 47 to 63Hz |
| Control DC Outputs | 0-20/4-20mA into 500 max, 0-10/0-5V into 500 min. Accuracy typically +/- 0.5% |
| Retransmit Outputs | 0-20/4-20mA into 500 max, 0-10/0-5V into 500 min. Accuracy typically +/- 0.25% |
| Communications | 2 Wire RS485, 1200 to 9600 Baud, West ASCII (Modbus Optional) |
| Dual Setpoint Selection | Selects between 2 SP’s using volt free or TTL input (SP1 = -0.6 to 0.8V, SP2 = 2 to 24V) |
| Operating & Environmental |  |
| Temperature & RH | 0 to 55°C (-20 to 80°C storage), 20% to 95%RH non-condensing |
| Power Supply | 90 to 264V 50/60Hz (optional 20 to 55V AC/22 to 65V DC), approx 4 Watts |
| Front Panel Protection | IEC IP66 (Behind panel protection is IP20) |
| Approvals and Certification | CE, UL & ULc |

PC Configuration Software: Runs on DOS or Windows 95/98. Includes connection cable.   Part Number M9997-A05011

110mm

48mm

45mm +0.5

45mm +0.5

48mm

10mm (approx)

### Dimensions

### Panel Cut-out

### Field Reconfiguration

### Connection Details

###### Input

Configurable to any type, no extra parts required

###### Output 1

Type is fixed as ordered. Either Relay/SSR (selectable), Triac or DC Linear (selectable for mV, mA, Volts)

###### Output 2

Configurable as Cool O/P or Alarm via plug-in Relay, SSR, Triac or DC Linear modules

###### Output 3

Configurable as Alarm via plug-in Relay or SSR modules, or retransmit using DC Linear module

###### Option Slot

Configurable as RS485 comms or dual setpoint selection, via plug-in modules

| ### Order Code | N6120 | - | x | - | x | - | x | - | x | - | xx | - | xxx |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

|  | ##### Input type |  |  | #### Special Variants |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 3 Wire RTD or DC mV | 1 |  |  | Blank | Special Variant not required |
|  | Thermocouple | 2 |  |  | S09 | MODBUS instead of West ASCII |
|  | DC mA | 3 |  |  |  | (requires RS485 option) |
|  | DC Voltage | 4 |  |  | S14 | 10V DC SSR outputs |
|  | Output 1 |  |  |  |  | (requires SSR output codes) |
|  | Relay Control | 1 |  |  |  |  |
|  | DC for SSR Control | 2 |  |  |  | Options and Power Supply |
|  | DC 0-10V Control | 3 |  |  | 00 | No Options/90-264V AC line supply |
|  | DC 0-20mA Control | 4 |  |  | 02 | No Options/24-48V AC or DC line supply |
|  | DC 0-5V SP Control | 5 |  |  | 10 | RS485 Comms/90-264V AC line supply |
|  | DC 4-20mA Control | 7 |  |  | 12 | RS485 Comms/24-48V AC or DC supply |
|  | Triac Control | 8 |  |  | 30 | Dual Setpoint/90-264V AC line supply |
|  | Output 2 |  |  |  | 32 | Dual Setpoint/24-48V AC or DC supply |
|  | Not fitted | 0 |  |  |  | Output 3 |
|  | Relay Control or Alarm 2 | 1 |  |  | 0 | Not fitted |
|  | DC for SSR Control or Alarm 2 | 2 |  |  | 1 | Relay Alarm 1 output |
|  | DC 0-10V Control | 3 |  |  | 2 | DC for SSR Alarm 1 output |
|  | DC 0-20mA Control | 4 |  |  | 3 | DC 0-10V Re-Transmit PV or SP |
|  | DC 0-5V Control | 5 |  |  | 4 | DC 0-20mA Re-Transmit PV or SP |
|  | DC 4-20mA Control | 7 |  |  | 5 | DC 0-5V Re-Transmit PV or SP |
|  | Triac Control | 8 |  |  | 7 | DC 4-20mA Re-Transmit PV or SP |

- In accordance with our policy of continuous improvement, we reserve the right to change specifications from those shown in this document.

- West Instruments Ltd

- The Hyde Business Park			  Tel: +44 (0)1273 606271

- Brighton, BN2 4JU			  Fax: +44 (0)1273 609990

- East Sussex			  e-mail: info@west-inst.co.uk

- England			  www.west-inst.co.uk