| West 6700 1/16 DIN Limit Alarm Unit |  |
| --- | --- |

|  | The West 6700 provides a programmable safety cut out with optional outputs for annunciators and alarms. A latched relay cuts power to the process if it exceeds the safe value. The unit must be reset before the process can continue. |  |
| --- | --- | --- |
|  | - High or low trip | - Exceed & relay indicators |
|  | - 5 amp latched relay | - Configuration via PC |
|  | - Remote reset option | - RS485 comms |
|  | - 2 Annunciators or alarms | - PV retransmit option |

## Technical Data

| Features |  |
| --- | --- |
| Output Configuration | Up to 3 Total. 1 latching trip relay, max 2 alarms relays, max 1 DC linear retransmit (PV or limit value) |
| Alarm 1 & 2 Types | Process high, process low, setpoint deviation, band, logical OR alarms or trip annunciator. |
| Limit Action | Latching relay output when PV exceeds set value. Selectable for high or low trip activation. |
| Output Reset Action | Limit output can be reset only when exceed condition is absent. Local or remote reset options. |
| Annunciator Reset Action | Annunciator output can be reset at any time. Local or remote reset options. |
| Human Interface | 4 button operation, dual 4 digit 10mm & 8mm high LED displays. Exceed, output & alarm indicators |
| PC Configuration | Off-line configuration from serial port to dedicated config socket (comms option not required) |
| # Input |  |
| Thermocouple | J, K, R, S, T, B, L, & N. |
| RTD | 3 Wire PT100, 50 per lead maximum (balanced) |
| DC Linear | 0-20/4-20mA, 0-50/10-50mV, 0-5/1-5/0-10/2-10V. Scaleable -1999 to 9999, dec point available |
| Impedance | >100M for Thermocouple and mV ranges, 47K for V ranges and 4.7 for mA ranges |
| Accuracy | +/- 0.25% of input span +/- 1 LSD (T/C CJC better than 0.7°C) |
| Sampling | 4 per second, 14 bit resolution approximately |
| Sensor Break Detection | <2 secs (except zero based DC ranges), control O/P’s turn off, high alarms activate for T/C and mV ranges, low alarms activate for RTD, mA or V ranges. |
| # Outputs & Options |  |
| Limit Trip Relay | Contacts SPDT 5Amp resistive at 240V AC, >100,000 operations |
| Alarm Relays | Contacts SPDT 2Amp resistive at 240V AC, >500,000 operations |
| Retransmit Outputs | 0-20/4-20mA into 500 max, 0-10/0-5V into 500 min. Accuracy typically +/- 0.25% |
| Communications | 2 Wire RS485, 1200 to 9600 Baud, West ASCII |
| Remote reset option | Allows remote latched relay and annunciator reset, using volt free or TTL input (Reset = -0.6 to 0.8V, or contact closure) |
| Operating & Environmental |  |
| Temperature & RH | 0 to 55°C (-20 to 80°C storage), 20% to 95%RH non-condensing |
| Power Supply | 90 to 264V 50/60Hz (optional 20 to 55V AC/22 to 65V DC), approx 4 Watts |
| Front Panel Protection | IEC IP66 (Behind panel protection is IP20) |
| Approvals and Certification | CE, UL & Ulc & FM |

110mm

48mm

45mm +0.5

45mm +0.5

48mm

10mm (approx)

### Dimensions

### Panel Cut-out

### Field Reconfiguration

### Connection Details

###### Input

Configurable to any type, no extra parts required

###### Output 1

Type is fixed as Limit Relay

###### Output 2

Configurable as Alarm or  Annunciator, via plug-in Relay

###### Output 3

Configurable as Alarm or Annunciator via plug-in Relay, or retransmit using DC Linear module

###### Option Slot

Configurable as RS485 comms or Remote Reset, via plug-in modules

| ### Order Code | N6700 | - | x | - | x | - | x | - | x | - | xx |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

|  | ##### Input type |  |  | Options and Power Supply |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 3 Wire RTD or DC mV | 1 |  |  | 00 | No Options/90-264V AC line supply |
|  | Thermocouple | 2 |  |  | 02 | No Options/24-48V AC or DC line supply |
|  | DC mA | 3 |  |  | 10 | RS485 Comms/90-264V AC line supply |
|  | DC Voltage | 4 |  |  | 12 | RS485 Comms/24-48V AC or DC supply |
|  |  |  |  |  | 30 | Remote Reset/90-264V AC line supply |
|  |  |  |  |  | 32 | Remote Reset /24-48V AC or DC supply |
|  | Output 1 |  |  |  |  | Output 3 |
|  | Limit Relay | 1 |  |  | 0 | Not fitted |
|  |  |  |  |  | 1 | Relay Alarm 1 or Annunciator |
|  |  |  |  |  | 3 | DC 0-10V Re-Transmit PV or SP |
|  | Output 2 |  |  |  | 4 | DC 0-20mA Re-Transmit PV or SP |
|  | Not fitted | 0 |  |  | 5 | DC 0-5V Re-Transmit PV or SP |
|  | Relay Alarm 2 or Annunciator | 1 |  |  | 7 | DC 4-20mA Re-Transmit PV or SP |

- In accordance with our policy of continuous improvement, we reserve the right to change specifications from those shown in this document.

- West Instruments Ltd

- The Hyde Business Park			  Tel: +44 (0)1273 606271

- Brighton, BN2 4JU			  Fax: +44 (0)1273 609990

- East Sussex			  e-mail: info@west-inst.co.uk

- England			  www.west-inst.co.uk